## CSF
Project |  | : | ARCH SAUD |  |  |  |  | System |  | : HVAC SYSTEM |  |  | Date :
Consultant |  | : | KG-MECH |  |  |  |  | Title |  | : AHU ESP Calculation |  |  | Rev. :
Contractor |  | : | [5 empty] | Prepared by |  | :
I. | Given Design Data;
| a. | Unit Ref. No. |  | : | FCU-1
| b. | FCU Air Quantity |  | : | 8750 | LPS |  | 18140 | CFM
| c. | Radius Elbow |  | : | R/D = 1.25
| d. | Initial Duct Size |  | : | 2000 | x | 550 | mm | 80 | x | 22
| e. | Grilles & Diffusers, (S.P.) |  | : | 0.1 | " wg.
II. | Reference;
| a. | IFC Drawing;
| b. | ASHRAE 2009 & SMACNA Cuts
ASHRAE Table & Chart, Fig. 9
ASHRAE/SMACNA Table 6
ASHRAE/SMACNA Table 10
III. | Calculation; (Equal Friction Loss Method)
External Static Pressure Required of (Supply Fan)
| a. | From Table-6, ASHRAE cuts, Equivalent Circular Diameter
|  | of --" x --" rectangular duct is equal to | [5 empty] | "Ø
| b. | From SMACNA/ASHRAE Table & Chart, Figure 9.
|  | _______ CFM air quantity @ ---"Ø dia, the Friction Rate is = | [8 empty] | 0.1 | " WG/ 100 Feet.
|  | Actual Initial Duct Velocity = |  |  | 1000 | FPM
| c. | Procedure of solving the Fittings Equivalent Length @ Design Condition R/D = 1.25
From Table-10, ASHRAE/SMACNA Cuts,
|  | Where; | For elbow size 64" x 32"
W = 64" & D = 32"
|  |  | W/D = 64/32 = 2.0 |  |  |  | Say; 3.0
From Table-10: L/D Ratio = 8 @ W/D = 3
Solving for L;
L/D = 8
L = 8 (32")
L = 8 (32") x (1'/12")
|  |  | L = 21.33 ft | Equivalent Length of fittings
* Apply above procedure simultaneously to other sizes to get the total length (duct + fittings)
IV. | Tabulation/Calculation Sheet
Turn to next page for the tabulation/calculation sheet

## ESP-FLAT_1-3
FCU STATIC PRESSURE CALCULATION SHEET | [10 empty] | W/D | L/D | @ R/D = 1.25
PROJ. NAME |  | ARCH SAUD | [5 empty] | FCUs Airflow (CFM) : | 8074 | 0 | 1 | 7
SYSTEM |  | : (Supply Fan) FALT:1-3 | [5 empty] | Actual Initial Velocity (FPM) : | 1000 |  | 3 | 8
DATE |  | : | [8 empty] | 6 | 12
SEC. | ITEM | COMPONENT | DUCT LENGTH IN (FEET) | FITTINGS EQUIVALENT LENGTH IN (FEET) | QTY | FRICTION LOSS ("WG/ 100 FT') ASHRAE Fig.9 | DUCTWORK FRICTION LOSS (IN. W.G.) | ADDITIONAL COMPONENT FRICTION LOSS (IN. W.G.) | TOTAL COMPONENT FRICTION LOSS (IN. W.G.)
A | 1. | Supply Ductwork | 106 | - | - | 0.1 | 0.106 | - | 0.106
| 2. | AHU's Sound Attenuator | - | - | 1 | - | - | 0.75 | 0.75
| 3. | Duct Fittings, 31" x 26" | - | 15 |  | 0.1 | 0 | - | 0
| 4. | Duct Fittings, 15" x 14" | - | 8 |  | 0.1 | 0 | - | 0
| 5 | Duct Fittings, 11" x 11" | - | 7 | 2 | 0.1 | 0.014 | - | 0.014
| 6. | Duct Fittings, 11" x 4" | - | 3 | 2 | 0.1 | 0.006 | - | 0.006
| 7. | Duct Fittings, 6" x 4" | - | 2 |  | 0.1 | 0 | - | 0
| 8. | Transition Fittings | - | 1 |  | 0.1 | 0 | - | 0
| 9. | Wye Branch Fittings | - | 0.5 | 1 | 0.1 | 0.0005 | - | 0.0005
| 10. | Single Duct VAV units with integral sound attenuator without reheat coil. | - | - | 0 | - | - | 0.4 | 0
| 11 | Grilles & Diffusers | - | - |  | - | - | 0.1 | 0
| 12 | Diffuser with HEPA Filter | - | - |  | - | - | 0.75 | 0
| 13 | HEPA Filter in the duct line | - | - | 1 | - | - | 0.65 | 0.65
| 14 | Carbon Filter in the duct line | - | - |  | - | - | 0.5 | 0
| 15 | Pre-insulated Flex. Duct | - | - |  | - | - | 0.025 | 0
| 16 | Automatic Damper | - | - |  | - | - | 0.15 | 0
| 17 | Fire Damper | - | - |  | - | - | 0.1 | 0
| 18 | Volume Control Damper | - | 0.5 | 2 | - | - | 0.1 | 0.2
| 22 | AHU Discharge Plenum | - | - |  | - | - | 0.1 | 0
Fan External Static Pressure (In W.G.) | [8 empty] | 1.7265
Safety Factor (%) | [8 empty] | 10
Fan Total External Static Pressure (In W.G.) | [8 empty] | 1.8991
Fan Total External Static Pressure (In Pa) | [8 empty] | 474.7875

## ESP-FLAT_2-4
FCU STATIC PRESSURE CALCULATION SHEET | [10 empty] | W/D | L/D | @ R/D = 1.25
PROJ. NAME |  | ARCH SAUD | [5 empty] | FCUs Airflow (CFM) : | 7564 | 0 | 1 | 7
SYSTEM |  | : (Supply Fan) FALT:2-4 | [5 empty] | Actual Initial Velocity (FPM) : | 1000 |  | 3 | 8
DATE |  | : | [8 empty] | 6 | 12
SEC. | ITEM | COMPONENT | DUCT LENGTH IN (FEET) | FITTINGS EQUIVALENT LENGTH IN (FEET) | QTY | FRICTION LOSS ("WG/ 100 FT') ASHRAE Fig.9 | DUCTWORK FRICTION LOSS (IN. W.G.) | ADDITIONAL COMPONENT FRICTION LOSS (IN. W.G.) | TOTAL COMPONENT FRICTION LOSS (IN. W.G.)
A | 1. | Supply Ductwork | 131 | - | - | 0.1 | 0.131 | - | 0.131
| 2. | AHU's Sound Attenuator | - | - | 1 | - | - | 0.75 | 0.75
| 3. | Duct Fittings, 30" x 26" | - | 15 | 1 | 0.1 | 0.015 | - | 0.015
| 4. | Duct Fittings, 16" x 14" | - | 8 | 1 | 0.1 | 0.008 | - | 0.008
| 5 | Duct Fittings, 16" x 10" | - | 6 | 1 | 0.1 | 0.006 | - | 0.006
| 6. | Duct Fittings, 16" x 6" | - | 4 | 3 | 0.1 | 0.012 | - | 0.012
| 7. | Duct Fittings, 8" x 4" | - | 3 | 2 | 0.1 | 0.006 | - | 0.006
| 8. | Transition Fittings | - | 1 | 3 | 0.1 | 0.003 | - | 0.003
| 9. | Wye Branch Fittings | - |  |  | 0.1 | 0 | - | 0
| 10. | Single Duct VAV units with integral sound attenuator without reheat coil. | - | - | 0 | - | - | 0.4 | 0
| 11 | Grilles & Diffusers | - | - |  | - | - | 0.1 | 0
| 12 | Diffuser with HEPA Filter | - | - |  | - | - | 0.75 | 0
| 13 | HEPA Filter in the duct line | - | - | 1 | - | - | 0.65 | 0.65
| 14 | Carbon Filter in the duct line | - | - |  | - | - | 0.5 | 0
| 15 | Pre-insulated Flex. Duct | - | - |  | - | - | 0.025 | 0
| 16 | Automatic Damper | - | - |  | - | - | 0.15 | 0
| 17 | Fire Damper | - | - |  | - | - | 0.1 | 0
| 18 | Volume Control Damper | - | 0.5 | 1 | - | - | 0.1 | 0.1
| 22 | AHU Discharge Plenum | - | - |  | - | - | 0.1 | 0
Fan External Static Pressure (In W.G.) | [8 empty] | 1.681
Safety Factor (%) | [8 empty] | 10
Fan Total External Static Pressure (In W.G.) | [8 empty] | 1.8491
Fan Total External Static Pressure (In Pa) | [8 empty] | 462.275